## color scheme
DISCOM NAME
REGULATION NAME WITH YEAR

## verification
State | Verification General Comments: | Status | Rectification Comments | Final Status
Gujarat | The ZIP contains the GERC Standards of Performance Regulations, 2023, notified on 6 December 2023. The regulation itself says it comes into force from publication and replaces the earlier 2005 framework. The dashboard nevertheless applies some 2023 specifications retrospectively to 2021-22 and 2022-23. Ex. voltage (2023 Regulation): LV: +6% / −6% HV: +6% / −9% EHV: +10% / −12.5% LT-system upgradation: 60 days HT/EHT upgradation: 180 days) wrong values for saidi, saifi and maifi in multiple sheets | Checked | cross checked with 2005 regulation, the standard for voltage remains same. Changed values for saifi, saidi and maifi | necessary changes made
Bihar | The 98% benchmark belongs to “Voltage Unbalance” in the overall performance standards, not clearly to the broader voltage-variation limits. The source requires voltage unbalance to remain within 3%, with at least 98% of such cases resolved within the prescribed period. I would therefore not retain 98% as the benchmark for the present “Voltage Variation” row without qualification. Also the 2 regulation acts post 2006 don't have source documents. | Checked | Amendment documents have been uploaded in the drive. Cross checked the voltage variation target. | necessary changes made
Andhra Pradesh | Portions of the AP tables refer to the “UPERC Electricity Supply Code”, which is a Uttar Pradesh instrument and therefore needs to be checked as a likely source/copying error rather than accepted at face value. The most important Andhra Pradesh corrections are therefore: remove unsupported SAIDI/SAIFI targets (20/72 and APCPDCL's 30/85); correct the reliability-index methodology; remove all UPERC references; correct the 8-hour/6-hour urban DT entries to 24 hours; separate the 3% Voltage Unbalance benchmark from the Voltage Variation indicator. | Checked | Reliability targets have been sourced from the separate order notified by the commission. Other changes have been cross checked. | necessary changes made
Karnataka | Specification of the regulations have been checked against the 2022 regulations and there are minor tweaks across all 5 discoms that I have flagged in a comment. | Checked | Cross-checked the target and standard of voltage variation which was highlighted. | necessary changes made
Madhya Pradesh | For the restoration period, the comment I've made needs to be changed across all 3 discoms as it a regulation-specific error. | Checked | 98.02 was added in place of 98.2. | necessary changes made
Maharashtra | Have to document and specify correct methodology for whenever conversions or any calculations have been done manually. Please double check for all 5 years and variables for this particular state. | Checked | Will cross check all the values. | unclear/needs more work
Rajasthan | SAIDI and SAIFI are quarterly/half-yearly regulatory indices, not annual standards. They are calculated for the entire licensee area using consumer-weighted 11-kV feeder data. The benchmarks are SAIDI 15 hours/quarter or 30 hours/six months and SAIFI 10 interruptions/quarter or 20 interruptions/six months. Voltage variation is incompletely specified in the PDFs. RERC requires LT +6%/−6%, HT +6%/−9%, EHT +10%/−12.5%, with four distinct resolution periods: 2 working days, 15 days, 60 days and 120 days, depending on infrastructure requirements. Could not locate a 3% EHT / 8% HT harmonics standard in the RERC 2021 SoP regulation. If those numbers came from a CEA/power-quality instrument, that source needs to be stated separately; they should not presently be attributed to RERC 2021. One evidence limitation remains: the RERC website confirms the existence of separate first-half and second-half SoP reports for each FY, but the underlying half-year PDFs were not retrievable through the source interface in this turn. I have therefore not treated every reported percentage/value as independently re-verified from the original half-year table; where a reported number is merely retained above, it means I found no regulatory inconsistency in its use, not that I independently reproduced it from the underlying RERC report. | Checked | Reliability values were been cross-checked with the quarterly data to ensure that standards have been met. Harmonics target removed. Only quarterly data available on the website. | necessary changes made
Telangana | There are therefore five high-priority Telangana corrections. First, change the regulation title to TSERC Regulation No. 5 of 2016. Second, redefine SAIDI/SAIFI/MAIFI using TSERC's monthly, connected-load-weighted 11/33-kV feeder methodology, including >5 minutes for sustained interruptions and ≤5 minutes for momentary interruptions. Third, separate Voltage Variation from Voltage Unbalance; a percentage of complaints resolved cannot be tested against a 3% voltage-unbalance limit. Fourth, harmonics should not be shown as regulatorily “N/A”: Regulation 5 contains a staged 3% / 8% / 8% THDV framework. Fifth, billing should read 24 working hours, not two working days, when no additional information is required, and complaint-resolution percentages must not be compared with the ≤0.1% faulty-bill rate. The official Commission page also confirms that SoP reports exist for both TGNPDCL and TGSPDCL for FY2021-22 to FY2024-25. | Checked | Checked the regulation it says - This Regulation may be called the Telangana State Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2016, so retained that only. Standard for billing complaint resolution - page 14 says - The Licensee shall resolve the complaint regarding electricity bills within 2 working days of its receipt, if no additional information is required to be collected.... but page 18 table says otherwise. We will have to confirm which one to retain. Definitions have been kept same for all states and discoms + cross checked with regulation. Standard definition has only been added. Added target for Harmonics as per source. | unclear/needs more work
Odisha | Billing has been mapped to the wrong reported variable. Comparable faulty-bill data exist and should be used against the 0.1% standard. TPCODL FY2021-22 rural DT compliance is wrongly marked “No”; 95.98% meets the 95% benchmark. FY2024-25 harmonics values of 8% LV/MV and 5% HV are not supported by the supplied OERC regulation. Voltage complaint data and voltage-limit-exceedance data should not be treated as the same metric. CAIDI is a derived analytical value, not an OERC-prescribed Overall SoP indicator, and its treatment should be made consistent across years. | Checked | Cross-checked the consumer complaints targets. We are adding CAIDI value only if stated explicitly in the performance data. | necessary changes made
Tamil Nadu | For Voltage Variation, the numerical voltage band currently used is correct, but “48 hours to 120 days depending on network needs” should be expanded into the actual three regulatory standards: 48 hours where no network expansion/enhancement is involved; 60 days where LT-network upgradation, transformer work or capacitor installation is required; and 120 days where HT-network upgradation is required. The overall-performance benchmark of 90% is correct. For billing, the 95% benchmark is correct, but the wording needs one qualification. The regulation says that billing complaints received before the due date are to be resolved before the next billing, while an arithmetic-error complaint must have been received at least three days before the due date for the requirement to correct it within the due date to apply. The present dashboard omits that condition. This should be changed for all the years. | Checked | Cross checked | necessary changes made
West Bengal | The 15-day / 6-month voltage standard is correct, but it covers persistent under/over-voltage complaints. The dashboard currently misses Regulation 10.2, which separately requires voltage-fluctuation complaints to be attended within 4 days in Urban areas and 8 days in Rural areas. I would therefore either split “Voltage Variation” into two rows or include both standards in the same specification field. The largest methodological correction concerns SAIDI, SAIFI and MAIFI. The WBERC SoP regulation does not itself define these three indices in the way the dashboard currently does. Instead, Regulation 9.7 requires detailed interruption reporting and says WBERC will use those data to perform reliability calculations and check compliance under the Tariff Regulations. Therefore, if you want SAIDI/SAIFI/MAIFI definitions in the dashboard, they need a separate Tariff-Regulation/reliability-methodology citation. MAIFI in particular should not presently be presented as though Regulation 46/WBERC explicitly prescribes it. -- maybe we can check with gaurav sir what to do about this. | Checked | Voltage fluctuation is not included as it is a separate indicator. | no changes necessary
Uttar Pradesh | The main correction is methodological: the dashboard currently mixes Guaranteed Standards with an Overall Standard benchmark of 95% for transformer failures. Under the SoP framework, these are separate layers. The guaranteed DT restoration times are 6 h Class-I Cities, 8 h Urban, 48 h Rural, whereas Schedule II's overall-performance provision requires at least 95% compliance against its own overall-standard time limits. The dashboard should not combine the guaranteed times with the overall 95% benchmark as though they are one standard. | Checked | Yes, there are different targets for guaranteed performance and overall performance. We are using the targets under guaranteed performance in the standard specified column and target under overall performance under benchmark column for the given indicator. | no changes necessary
No. | Doubts | Status | Added Comments | Final Status
1 | The distinction between standard specified and benchmark is unclear. I'm not sure why they're in different units also. |  | Standard specified in the time period in which the complaint/ issue is to be resolved, whereas benchmark is the minimum % of complaints that must be resolved within the standard specified.
2 | What do we do when it comes to different formulas for SAIDI, SAIFI and MAIFI? For ex. West Bengal, Telangana
3 | When it comes to LV, EHV and HV do we separate these benchmarks and reported data? or do we only consider LV for consumers?
4 | Difference between Voltage variation, unbalance and fluctuation and whether these can be used as proxies
5 | What are the appropriate conversions for quarterly to annual indicators? For ex. Maharasthra calculations

## MSEDCL,MAHARASHTRA
Maharashtra State Electricity Distribution Company Limited
Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) Regulations, 2021 | Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) (First Amendment) Regulations, 2024. |  | https://docs.google.com/spreadsheets/d/1WiH3YByOIBIlNMMwlLJL3QBUUeMguZ8iPjf-duj7b-s/edit?gid=1079041780#gid=1079041780
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 221.62 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1.4 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Standard for momentary outages was not yet effective for 2021-22 cycle. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 158.37 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI HT | Average restoration time for those HT consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 86.75 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 13.6 | % of cases resolved within specified time/standard | No | N/A | Different standard metric | Performance std has been met at all times.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | N/A | N/A | 74.55 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | N/A | N/A | 18.29 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | N/A | N/A | 23.16 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 143.05 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.53 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 56.46 | Average minutes taken to restore supply for each interruption event over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI HT | Average restoration time for those HT consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 80.58 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | NO | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 149.85 | Total minutes of supply interruption for an average consumer over two quarters | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.63 | Total number of sustained interruptions for an average consumer over two quarters | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Momentary outages of 5 minutes or less are not currently taken into account for reliability indices. | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 57.06 | Average minutes taken to restore supply for each interruption event over two quarters | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI HT | Average restoration time for those HT consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 78.71 | Average minutes taken to restore supply for each interruption event over two quarters | No | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 78.58 | % of cases resolved within specified time/standard | No | N/A | Different standard metric.
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs of receipt or during the subsequent billing cycle. | N/A | N/A | 96.9 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | N/A | N/A | 50.55 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | N/A | N/A | 60.15 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 105.39 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1.13 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Standard for momentary outages was introduced in the 2024 Amendment. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 93.54 | Average minutes taken to restore supply for each interruption event over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI HT | Average restoration time for those HT consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 87.81 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 63.29 | % of cases resolved within specified time/standard. | No | N/A | Different standard metric
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers. | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | N/A | N/A | 92.11 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | N/A | N/A | 56.15 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | N/A | N/A | 61.57 | % of cases resolved within specified time/standard. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 127.51 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1.39 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Standard for momentary outages was not yet effective for 2022-23 cycle. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 91.58 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI HT | Average restoration time for those HT consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 86.06 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 22.09 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | N/A | N/A | 85.26 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | N/A | N/A | 24.24 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | N/A | N/A | 26.65 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.

## DGCVL,GUJARAT
Dakshin Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 379 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.61 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.13 | Total number of momentary interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 82.21 | Average restoration time (Minutes) for interrupted consumers over the year | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 5.81 |  | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 82.15 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 359 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 7.46 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.25 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 49 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | N/A | NO | N/A | Data not provided.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | N/A | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 251 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 6.39 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.85 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 39 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | % failure rate of Distribution transformer for the year. | NO | N/A | Data not provided.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | % of cases resolved within specified time/standard during the year. | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 256 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.19 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 6.82 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 6.11 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.65 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 339 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.38 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.23 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 77.33 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 6.27 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## UGVCL,GUJARAT
Uttar Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 182.56 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.51 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 5.39 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 72.83 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | Reported data not available.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | LV : 2.89; HV : 0.71; EHV : 0.0 | % compliance | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | LT : 0.7; HT : 0.0; EHT : 0.0 | % compliance | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 6.88 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 22.28; 34.42 | % of cases resolved within stipulated time : For current bills where no additional information is required; Where additional information relating to correctness of reading etc. is required | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 128.4 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 7.09 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.65 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 57 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | Reported data not available.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | LV : 97.68%; HV : 99.02%; EHV : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT : 99.73%; HT : 97.61%; EHT : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 7.11 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 96.33; 97.42 | % of cases resolved within stipulated time : For current bills where no additional information is required; Where additional information relating to correctness of reading etc. is required | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 134.28 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.76 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 5.6 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 48.72 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | Reported data not available.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | LV : 98.49%; HV : 99.49%; EHV : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT : 99.79%; HT : 98.36%; EHT : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.72 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 95.01; 92.78 | % of cases resolved within stipulated time : For current bills where no additional information is required; Where additional information relating to correctness of reading etc. is required | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 152.9 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.3 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.61 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 66.41 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | Reported data not available.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | LV : 97.26%; HV : 99.33%; EHV : 100.00% | % compliance | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT : 99.91%; HT : 99.62%; EHT : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 7.34% | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 43.45%; 49.77% | % of cases resolved within stipulated time : For current bills where no additional information is required; Where additional information relating to correctness of reading etc. is required | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 134.79 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.06 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.53 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 65.42 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | Reported data not available.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | LV : 97.12%; HV : 99.47%; EHV : 100.00% | % compliance | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | LT : 99.91%; HT : 99.88%; EHT : 100.00% | % compliance | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 6.84 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 25.74; 44.28 | % of cases resolved within stipulated time : For current bills where no additional information is required; Where additional information relating to correctness of reading etc. is required | NO | N/A | No benchmark defined in regulations.

## MGVCL,GUJARAT
Madhya Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 288 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.79 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 9.82 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Data not reported.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 5.39 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 50.39 | % of cases resolved within specified time/standard. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 25 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12.28 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 18.41 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.36 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.22 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | N/A | NO | N/A | Reported data is 45,570 pages long and not machine readable so the reported values could not be fetched.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 292 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.84 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 14.36 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 67.56 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.44 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 265 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.51 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 9.62 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 75.5 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 4.93 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## PGVCL,GUJARAT
Paschim Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12548 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 95.34 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 114.17 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 131.61 | Average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | LT, EHT : Not reported! HT : 0.0 | % Compliance | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 2.8 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 41.44 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 680 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 13.23 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.96 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 11 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT, EHT : #DIV/0! HT : 100 | % Compliance | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 9.32 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 92.43 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 757 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12.03 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 11.29 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT, EHT : #DIV/0!; HT : 0.31 | % Compliance | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | % failure rate of Distribution transformer for the year. | NO | N/A | Data not provided.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | % of cases resolved within specified time/standard during the year. | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10762 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 100.48 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 96.03 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 107.11 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | LT, EHT : 0 HT : 10.13 | % Compliance | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 10.8 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 99.67 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3024 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 30.72 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Data not reported.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 98.44 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensees must monitor HT consumers at strategic points. | N/A | N/A | LT, EHT : 0 HT : 10.13 | % Compliance | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 1 day in Urban areas and 3 days in Rural areas. | N/A | N/A | 11.6 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 99.79 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## AVVNL,RAJASTHAN
Ajmer Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 2208 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 31.07 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 98.98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.11 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.12 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 1083 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 15.7 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 94.3% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | N/A | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.4 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 97.61 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 1139.4 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 16.17 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 96.19% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | N/A | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.89% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 95.83% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter | N/A | N/A | 5.38 | Average hours of supply interruption for an average consumer per quarter. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter | N/A | N/A | 4.52 | Average number of sustained interruptions for an average consumer per quarter. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 96.92 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 8 hrs (Class-1/Urban), 24 hrs (Rural) | 90 | % of cases to be resolved within specified time/standard. | 99.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Within 3 working days (no info needed) or 7 working days (if info needed) | 90 | % of cases to be resolved within specified time/standard. | 98.54 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 8.12 | Average hours of supply interruption for an average consumer per quarter. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 7.3 | Average number of sustained interruptions for an average consumer per quarter. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 97.27 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.34 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.39 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JVVNL,RAJASTHAN
Jaipur Vidyut Vitran Nigam Limited |  | THE ANNUAL VALUE FOR SAIDI & SAIFI IS THE SUM TOTAL OF QUARTERLY VALUES. ANNUAL VALUE AS PER THE FORMULA GIVEN IN THE REGULATION COULD NOT BE DERIVED DUE TO LIMITED DATA IN THE PERFORMANCE REPORTS.
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1307.4 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 12.15 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 97.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.78 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.36 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 424.44 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 14.65 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 99.26 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.24 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.92 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 444.36 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 15.18 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 96.18 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | N/A | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.28 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | N/A | 378.8 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | N/A | 13.84 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 98.49 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 97.46 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 97.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 258.23 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 10.47 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 99.46 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.29 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 99.17 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JdVVNL,RAJ
Jodhpur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1307 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 12.15 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 97.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.78 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.36 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | N/A | 831 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | N/A | 13.46 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 99.5 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly duration limits set by the Commission. | 608.4 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly frequency limits set by the Commission. | 12.56 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 94.74 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | N/A | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 96.6 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Fifteen hours per consumer per quarter | N/A | N/A | 3.18 | Total hours of supply interruption for an average consumer over the year | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Ten interruptions per consumer per quarter | N/A | N/A | 3.56 | Total number of sustained interruptions for an average consumer over the year | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 95.11 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 8 hrs (Class-1/Urban), 24 hrs (Rural) | 90 | % of cases to be resolved within specified time/standard. | 97.88 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Within 3 working days (no info needed) or 7 working days (if info needed) | 90 | % of cases to be resolved within specified time/standard. | 98.82 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1694.85 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIDI)
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 24.34 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | Different standard metric. (No benchmark for annual SAIFI)
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 working days if no network work needed; 15 days if LT augmentation/DT capacity enhancement needed; 60 days new DT substation; 120 days new/augmented 33/11-kV substation.. | 90 | % of cases to be resolved within specified time/standard. | 98.25 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 97.44 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.58 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## TPCODL,ODISHA
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 9304 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 378 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 85 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 95.98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 12.4 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark MEANING | Reported data | REPORTED DATA MEANING | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 12600 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 248 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 77 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 50.81 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 96.55 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 16.94 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 10559 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 312 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 34 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 95 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | N/A | N/A | 9.2 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 8243 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 341 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 53 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | N/A | N/A | 33.43 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.

## TPNODL,ODISHA
Tata Power North Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 27331 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 680 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 209 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 19459 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 526 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 143 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 36.99 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 20937 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 576 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 107 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 22703 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 621 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 25 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | N/A | N/A | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.

## TPSODL,ODISHA
Tata Power South Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 9337 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 234 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 16282 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 316 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 130 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 51.53 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 16045 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 326 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 54 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 7647 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 225 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 34 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | N/A | N/A | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.

## TPWODL,ODISHA
Tata Power West Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 25441 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 600 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 66 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 98.37 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 94.71 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 96.04 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 20684 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 424 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 62 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 48.78 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 0.08 | % cases exceeding voltage limits for EHT and LT. | No | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 96.39 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 85.01 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 91.46 | % of cases resolved within specified time/standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 18312 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 428 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 43 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 9 | Nine cases exceeding voltage limits for HT. | No | N/A | No benchmark defined in regulations for number of cases.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 98.7 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 85.75 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | N/A | N/A | 94.48 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 19770 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 468 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Target levels to be notified annually by the Commission | N/A | N/A | 40 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | The distribution licensee must maintain voltage within the prescribed limits: LV: +6%/-6%; HV: +6%/-9%; EHV: +10%/-12.5% of declared voltage. Improve voltage variation within 15 days of the original complaint if no expansion/ enhancement is required. Resolve within 120 days in case upto 11KV, and 180 days in case upto 33KC | N/A | N/A | 1.5 | Cases exceeding voltage limits for HT were reported. | No | N/A | No benchmark defined in regulations for case quantity.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 99.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 97.33 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | N/A | N/A | 82.56 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | No benchmark defined in regulations.

## TGNPDCL, TELANGANA
Northern Power Distribution Company of Telangana Limited
Telangana State Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2016.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 2760 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of sustained interruptions per consumer for the year | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 70 | Total number of momentary interruptions per consumer for the year | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2021-22 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 100 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 1695 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 42 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 42.85 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2025-26 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 99.97 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | N/A | N/A | 99.88 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 5509.2 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 51 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2024-25 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 99.91 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | N/A | N/A | 99.73 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 10272 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 61 | Total number of sustained interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 68 | Total number of momentary interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2023-24 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 100 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | N/A | N/A | 99.71 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2022-23 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 100 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | N/A | N/A | 99.65 | % of cases resolved within specified time/standard | Yes | Yes | N/A

## TGSPDCL, TELANGANA
Southern Power Distribution Company of Telangana Limited
Telangana State Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2016.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 2760 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 70 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2021-22 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 100 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2021-22 | Restoration of Supply | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 427.46 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 18.7 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 14.31 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2025-26 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | N/A | N/A | No | N/A | Overall Standard Data is not reported.
2025-26 | Restoration of Supply | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 5509.2 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 51 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2024-25 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | N/A | N/A | No | N/A | Overall Standard Data is not reported.
2024-25 | Restoration of Supply | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Data is not readable.
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Data is not readable.
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Data is not readable.
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not readable.
2023-24 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | N/A | N/A | No | N/A | Data is not readable.
2023-24 | Restoration of Supply | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | N/A | N/A | No | N/A | Data is not readable.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | ≤3% at 132 kV and above; ≤8% at 33 kV; ≤8% at 11 kV. | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2022-23 | Restoration of Supply | Distribution Transformer Failure | Restoration of supply through replacement of the distribution transformer following its failure. | Cities & towns: 24 hours; Rural: 48 hours | 95 | % of DTRs replaced within the specified time limits | 97.18 | % of DTRs replaced within the specified time limits | Yes | Yes | N/A
2022-23 | Restoration of Supply | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no information needed) or 7 working days (if information needed). | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric

## MPEZ,MADHYA PRADESH
Madhya Pradesh Poorv Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT and 8% for HT consumers | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPCZ, MADHYA PRADESH
Madhya Pradesh Madhya Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 98.02 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPWZ,MADHYA PRADESH
Madhya Pradesh Paschim Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bills | Time period within which bills are to be served (Urban) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to urban consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bills | Time period within which bills are to be served (Rural) | This refers to the duration before the payment due date by which electricity bills must be delivered and served to the consumers . | The distribution licensee must serve electricity bills to rural consumers before 15 days of the due date . | N/A | N/A | 100 | % of cases resolved within specified time/standard | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## CESC, KARNATAKA
Chamundeshwari Electricity Supply Corporation Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## BESCOM, KARNATAKA
Bangalore Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | Minimum percentage of cases that must be resolved within the specified 7-day time limit | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## HESCOM, KARNATAKA
Hubli Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## GESCOM, KARNATAKA
Gulbarga Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## MESCOM, KARNATAKA
Mangalore Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution within 7 days if no network expansion/enhancement is required; 120 days if distribution-system upgradation is required | 95 - no expansion cases; 90 - system upgradation is required | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## TANGEDCO, TAMIL NADU
Tamil Nadu Generation and Distribution Corporation Limited
TAMIL NADU ELECTRICITY DISTRIBUTION STANDARDS OF PERFORMANCE REGULATIONS, 2004 (As amended upto 31-03-2024)
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours if no network expansion/enhancement; 60 days if LT network upgradation/transformer/capacitor work; 120 days if HT network upgradation is required. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Billing complaints received before the due date shall be resolved before the next billing, with refund/adjustment if any. Arithmetic errors received at least three days prior to the due date shall be corrected within the due date | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours if no network expansion/enhancement; 60 days if LT network upgradation/transformer/capacitor work; 120 days if HT network upgradation is required. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Billing complaints received before the due date shall be resolved before the next billing, with refund/adjustment if any. Arithmetic errors received at least three days prior to the due date shall be corrected within the due date | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours if no network expansion/enhancement; 60 days if LT network upgradation/transformer/capacitor work; 120 days if HT network upgradation is required. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Billing complaints received before the due date shall be resolved before the next billing, with refund/adjustment if any. Arithmetic errors received at least three days prior to the due date shall be corrected within the due date | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours if no network expansion/enhancement; 60 days if LT network upgradation/transformer/capacitor work; 120 days if HT network upgradation is required. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Billing complaints received before the due date shall be resolved before the next billing, with refund/adjustment if any. Arithmetic errors received at least three days prior to the due date shall be corrected within the due date | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours if no network expansion/enhancement; 60 days if LT network upgradation/transformer/capacitor work; 120 days if HT network upgradation is required. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Billing complaints received before the due date shall be resolved before the next billing, with refund/adjustment if any. Arithmetic errors received at least three days prior to the due date shall be corrected within the due date | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## NBPDCL, BIHAR
North Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | THD at connection point shall not exceed 5% (with no single harmonic above 3%),THD for current drawn from the transmission/sub-transmission system at the connection point shall not exceed 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | THD at connection point shall not exceed 5% (with no single harmonic above 3%),THD for current drawn from the transmission/sub-transmission system at the connection point shall not exceed 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | THD at connection point shall not exceed 5% (with no single harmonic above 3%),THD for current drawn from the transmission/sub-transmission system at the connection point shall not exceed 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | THD at connection point shall not exceed 5% (with no single harmonic above 3%),THD for current drawn from the transmission/sub-transmission system at the connection point shall not exceed 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | THD at connection point shall not exceed 5% (with no single harmonic above 3%),THD for current drawn from the transmission/sub-transmission system at the connection point shall not exceed 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## SBPDCL, BIHAR
South Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7 working days of receipt of Complaint (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## WBSEDCL, WEST BENGAL
West Bengal State Electricity Distribution Company Limited
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) Regulations, 2010
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) (First Amendment) Regulations, 2013.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available

## DPL, WEST BENGAL
The Durgapur Projects Limited
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) Regulations, 2010
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) (First Amendment) Regulations, 2013.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available

## PVVNL, UP
Paschimanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019 |  | Same regulatory changes as next sheet
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
2 days where fault is a local transformer problem; 10 days where no network expansion/enhancement is required; 120 days where distribution-system upgradation is required. If a new substation is required, a proposal must be submitted to the Commission within one month and the consumer informed of likely resolution time will be added for voltage variation target.

## MVVNL,UP
Madhyanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019 |  | Same regulatory changes as previous sheet
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## DVVNL,UP
Dakshinanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## PuVVNL,UP
Purvanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019 |  | Same regulatory changes as previous sheet
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## KESCO,UP
Kanpur Electricity Supply Company
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019 |  | Same regulatory changes as previous sheet
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APSPDCL, AP
Southern Power Distribution Company of Andhra Pradesh Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours of receiving a complaint in cities and towns. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours of receiving a complaint in cities and towns. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APEPDCL,AP
Eastern Power Distribution Company of Andhra Pradesh Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%.N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours of receiving a complaint in cities and towns. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APCPDCL,AP
Andhra Pradesh Central Power Distribution Corporation Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 30 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 85 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | Low Voltage: +6% and -6%; High Voltage: +6% and -9%; Extra High Voltage: +10% and -12.5% | Maintain voltage within the permissible limit | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours of receiving a complaint in cities and towns. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available