## color scheme
DISCOM NAME
REGULATION NAME WITH YEAR

## MSEDCL,MAHARASHTRA
Maharashtra State Electricity Distribution Company Limited
Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) Regulations, 2021 | Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) (First Amendment) Regulations, 2024.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 887.54 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 5.6 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Standard for momentary outages was not yet effective for 2021-22 cycle. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 624.24 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 13.6 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | 99 | % of cases to be resolved within specified time/standard | 74.55 | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | 90 | % of cases to be resolved within specified time/standard | 18.29 | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | 90 | % of cases to be resolved within specified time/standard | 23.16 | % of cases resolved within specified time/standard | Yes | No | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 573 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.15 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 56.45 | Average minutes taken to restore supply for each interruption event over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | NO | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | NO | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | NO | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | NO | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 598.88 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained interruptions per consumer occurring during the reporting period | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.48 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of 5 minutes or less are not currently taken into account for reliability indices. | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2024-25 | Reliability of Supply | CAIDI | Average interruption duration of the sustained interruptions for those who experienced interruptions during the reporting period | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 57.15 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 78.58 | % of cases resolved within specified time/standard | No | N/A | Different standard metric.
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs of receipt or during the subsequent billing cycle. | 99 | % of cases to be resolved within specified time/standard | 96.9 | % of cases resolved within specified time/standard | Yes | No | N/A
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | 90 | % of cases to be resolved within specified time/standard | 50.55 | % of cases resolved within specified time/standard | Yes | No | N/A
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | 90 | % of cases to be resolved within specified time/standard | 60.15 | % of cases resolved within specified time/standard | Yes | No | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 105.51 | Total minutes of supply interruption for an average consumer over the year. [52, 66, 83, 84-Annexure VII] | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1.125 | Total number of sustained interruptions for an average consumer over the year. [52, 66, 83, 84-Annexure VII] | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Standard for momentary outages was introduced in the 2024 Amendment. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 94.17 | Average minutes taken to restore supply for each interruption event over the year. [52, 66, 83, 84-Annexure VII] | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | 100 | % of time the grid must remain stable within the specified limits | 63.29 | % of cases resolved within specified time/standard. [43, 57, 74, 84-Annexure III] | No | N/A | Different standard metric
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers. | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | 99 | % of cases to be resolved within specified time/standard | 92.11 | % of cases resolved within specified time/standard. [43, 57, 74, 84-Annexure III] | Yes | No | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | 90 | % of cases to be resolved within specified time/standard | 56.15 | % of cases resolved within specified time/standard. [43, 57, 74, 84-Annexure III] | Yes | No | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | 90 | % of cases to be resolved within specified time/standard | 61.57 | % of cases resolved within specified time/standard. [43, 57, 74, 84-Annexure III] | Yes | No | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1533.01 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 16.73 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Standard for momentary outages was not yet effective for 2022-23 cycle. | N/A | N/A | N/A | N/A | No | N/A | Reporting mandated starting July 2024.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 91.63 | Average minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | % of time the grid must remain stable within the specified limits | 100 | 22.09 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT & 8% for HT consumers | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | % of cases to be resolved within specified time/standard | 99 | 85.26 | % of cases resolved within specified time/standard | Yes | No | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | % of cases to be resolved within specified time/standard | 90 | 24.24 | % of cases resolved within specified time/standard | Yes | No | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | % of cases to be resolved within specified time/standard | 90 | 26.65 | % of cases resolved within specified time/standard | Yes | No | N/A

## DGCVL,GUJARAT
Dakshin Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 379 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.61 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.13 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 82.21 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.81 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 82.15 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 359 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 7.46 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.25 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 49 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | N/A | NO | N/A | Data not provided.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | N/A | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 251 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 6.39 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.85 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 39 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | % failure rate of Distribution transformer for the year. | NO | N/A | Data not provided.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | % of cases resolved within specified time/standard during the year. | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3049 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 48.37 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 77.47 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 63.03 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.65 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4067 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 52.59 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 98.71 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 77.33 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.27 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## PGVCL,GUJARAT
Paschim Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12548 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 95.34 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 114.17 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 131.61 | Average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 2.8 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 41.44 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 680 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 13.23 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.96 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 11 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 9.32 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 92.43 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 757 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12.03 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 11.29 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 0.31 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | N/A | % failure rate of Distribution transformer for the year. | NO | N/A | Data not provided.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | N/A | % of cases resolved within specified time/standard during the year. | NO | N/A | Data not provided.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10762 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 100.48 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 96.03 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 107.11 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 89.87 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 10.8 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 99.67 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3024 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 30.72 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 33.19 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 98.44 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 89.87 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 11.6 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 99.79 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## MGVCL,GUJARAT
Madhya Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 288 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.79 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 9.82 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | N/A | N/A | NO | N/A | Data not reported.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.39 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 50.39 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 25 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 12.28 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 18.41 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.36 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.3 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 25.04 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.16 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 17.64 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.1 | Average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 0 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 0 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 3.61 | % failure rate of Distribution transformer for the year. | NO | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 99.15 | % of cases resolved within specified time/standard during the year. | NO | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 327 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.84 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 14.36 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 67.56 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.44 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 265 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.51 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 9.62 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 75.5 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 4.93 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## UGVCL,GUJARAT
Uttar Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023. | Gujarat Electricity Regulatory Commission (Standard of Performance of Distribution Licensee) Regulations, 2005
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2193 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 30.14 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 64.73 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 72.76 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 97.11 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 99.93 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.88 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 29.66 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 134 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 7.09 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 8.65 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 57 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 2.32 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 0.27 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 7.11 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 96.13 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average duration of sustained interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 134 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average frequency of sustained power interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 2.76 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions per consumer occurring during the reporting period. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 5.6 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 58 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 1.51 | % of sample tests showing NIL deviation from prescribed standards (Low Voltage). | NO | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 0.21 | % of sample tests showing NIL deviation from prescribed standards (LT Consumers). | NO | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.72 | % failure rate of Distribution transformer for the year. | NO | N/A | No benchmark defined in regulations.
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 92.29 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1839 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 27.71 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 55.43 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 66.37 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 97.26 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 99.91 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 7.34 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 1615 | Total minutes of supply interruption for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 24.74 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 54.26 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 65.28 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 97.12 | % of sample tests showing NIL deviation from prescribed standards. | No | N/A | No benchmark defined in regulations.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 99.91 | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.84 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day; 10 days (info needed); 15 days (site visit). | N/A | N/A | 100 | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## AVVNL,RAJASTHAN
Ajmer Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 2208 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 31.07 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 98.98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.11 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.12 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 1083 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 15.7 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 94.3% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT. | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.4 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 97.61 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 1139.4 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 16.17 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 96.19% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT. | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.89% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 95.83% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter | N/A | N/A | 5.38 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter | N/A | N/A | 4.52 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT) | Resolve within 2 to 120 days depending on required work | 90 | % of cases to be resolved within specified time/standard. | 96.92 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 8 hrs (Class-1/Urban), 24 hrs (Rural) | 90 | % of cases to be resolved within specified time/standard. | 99.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Within 3 working days (no info needed) or 7 working days (if info needed) | 90 | % of cases to be resolved within specified time/standard. | 98.54 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 8.12 | Average hours of supply interruption for an average consumer per quarter. | Yes | Yes | N/A
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 7.3 | Average number of sustained interruptions for an average consumer per quarter. | Yes | Yes | N/A
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 97.27 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.34 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.39 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JVVNL,RAJASTHAN
Jaipur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1307 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 12.15 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 97.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.78 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.36 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 424 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 14.65 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 99.26 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.24 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.92 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly/Half-yearly duration limits set by the Commission. | 444.36 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly/Half-yearly frequency limits set by the Commission. | 15.18 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 96.18 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT. | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98.28 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | N/A | 378.8 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | N/A | 13.84 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 98.49 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 97.46 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 97.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 258.23 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 10.47 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 99.46 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.29 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 99.17 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JdVVNL,RAJ
Jodhpur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1307 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 12.15 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 97.43 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.78 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.36 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | N/A | 831 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | N/A | 13.46 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2025-26 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 99.5 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a year. | Thirty hours per consumers per six months or fifteen hours per consumer per quarter. | N/A | Quarterly duration limits set by the Commission. | 608.4 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a year. | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter. | N/A | Quarterly frequency limits set by the Commission. | 12.56 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% for LT; +6% to -9% for HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 94.74 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply. | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT. | N/A | N/A | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Performance data not reported.
2024-25 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 96.6 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Fifteen hours per consumer per quarter | N/A | N/A | 3.18 | Total hours of supply interruption for an average consumer over the year | Yes | Yes | N/A
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Ten interruptions per consumer per quarter | N/A | N/A | 3.56 | Total number of sustained interruptions for an average consumer over the year | Yes | Yes | N/A
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT) | Resolve within 2 to 120 days depending on required work | 90 | % of cases to be resolved within specified time/standard. | 95.11 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported
2023-24 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 8 hrs (Class-1/Urban), 24 hrs (Rural) | 90 | % of cases to be resolved within specified time/standard. | 97.88 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Within 3 working days (no info needed) or 7 working days (if info needed) | 90 | % of cases to be resolved within specified time/standard. | 98.82 | % of cases resolved within specified time/standard during the year | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 1694.85 | Total minutes of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 24.34 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -6% (LT), +6% to -9% (HT)). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 98.25 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 97.44 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.58 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## TPCODL,ODISHA
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 9304 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 378 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 85 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 95.98 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 12.4 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark MEANING | Reported data | REPORTED DATA MEANING | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 12600 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 248 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 77 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 50.81 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 96.55 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 16.94 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 10559 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 312 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 34 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5% | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 95 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued | 9.2 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 8243 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 341 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 53 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5% | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued | 33.43 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric

## TPNODL,ODISHA
Tata Power North Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 27331 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 680 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 209 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 19459 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 526 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 143 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 36.99 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within: ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | % error rate | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 20937 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 576 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 107 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 22703 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 621 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 25 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5% | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 98 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric

## TPSODL,ODISHA
Tata Power South Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 9337 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 234 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 16282 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 316 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 130 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 51.53 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0 | zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within: ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | % error rate | 100 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 16045 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 326 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 54 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT. | No | N/A | No complaints were received or registered during the year.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 7647 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 225 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 34 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5% | N/A | N/A | 0 | Zero cases exceeding voltage limits for EHT and LT were reported. | No | N/A | No complaints were received or registered during the year.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued | 100 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric

## TPWODL,ODISHA
Tata Power West Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004 | Orissa Electricity Regulatory Commission (Licensee’s Standard of Performance) (1st Amendment) Regulations, 2010.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 25441 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 600 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 66 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 98.37 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | 94.71 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 96.04 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas . | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 48 hours in Rural areas. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 20684 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 424 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 62 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 48.78 | Total minutes of restoration time for consumers who experienced interruptions. | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 0.08 | % cases exceeding voltage limits for EHT and LT. | No | N/A | No benchmark defined in regulations.
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2024-25 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % target | 96.39 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2024-25 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % target | 85.01 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | % error rate | 91.46 | % of cases resolved within specified time/standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 18312 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 428 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 43 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5%. | N/A | N/A | 9 | Nine cases exceeding voltage limits for HT. | No | N/A | No benchmark defined in regulations for number of cases.
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV. | N/A | N/A | N/A | No data furnished by the licensee. | No | N/A | No benchmark defined in regulations.
2023-24 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas. | 95 | % of cases to be resolved within specified time/standard. | 98.7 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2023-24 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard. | 85.75 | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 94.48 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 19770 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 468 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Target levels to be notified annually by the Commission | N/A | N/A | 40 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | Data for average restoration time not listed in the overall standard reporting table. | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ±6%; HV: +6% to -9%; EHT: +10% to -12.5% | N/A | N/A | 1.5 | Cases exceeding voltage limits for HT were reported. | No | N/A | No benchmark defined in regulations for case quantity.
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within ≤ 8% for LV/MV; ≤ 5% for HV | N/A | N/A | N/A | No data furnished by the licensee for this period. | No | N/A | No benchmark defined in regulations.
2022-23 | Restoration of Supply | DT Failure: Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 24 hours in Urban areas | 95 | % of cases to be resolved within specified time/standard | 99.08 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Restoration of Supply | DT Failure: Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement within 48 hours in Rural areas | 95 | % of cases to be resolved within specified time/standard | 97.33 | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt | 0.1 | Maximum allowable percentage of faulty bills relative to the total number of bills issued | 82.56 | % of complaints resolved within the specified 30-day time standard during the year. | No | N/A | Different standard metric

## TGNPDCL, TELANGANA
Northern Power Distribution Company of Telangana Limited
TELANGANA STATE ELECTRICITY REGULATORY COMMISSION REGULATION No. 2016 LICENSEES’ STANDARDS OF PERFORMANCE
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 2760 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of sustained interruptions per consumer for the year | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 70 | Total number of momentary interruptions per consumer for the year | No | N/A | Benchmark not notified.
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | No | Yes | Different standard metric
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.96 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 1695 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 42 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 42.85 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | Yes | N/A | Different standard metric
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 99.85 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.56 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 99.88 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 5509.2 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 51 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.91 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 99.73 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 10272 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 61 | Total number of sustained interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 68 | Total number of momentary interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 98.82 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.04 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 99.71 | % of cases resolved within specified time/standard | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.78 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 99.65 | % of cases resolved within specified time/standard | Yes | Yes | N/A

## TGSPDCL, TELANGANA
Southern Power Distribution Company of Telangana Limited
TELANGANA STATE ELECTRICITY REGULATORY COMMISSION REGULATION No. 2016 LICENSEES’ STANDARDS OF PERFORMANCE
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 2760 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 70 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Performance data is not reported.
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.96 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 100 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 427.46 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 18.7 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 14.31 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 98.87 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | No | Performance data is not reported.
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 98.12 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 96.89 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 86.11 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 5509.2 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 51 | Total number of sustained interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 66 | Total number of momentary interruptions per consumer for the year | No | N/A | No benchmark defined in regulations.
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 100 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 99.91 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 99.73 | % of cases resolved within specified time/standard | No | N/A | Different standard metric
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 894.55 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 33.79 | Total number of sustained interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | 17.6 | Total number of momentary interruptions per consumer for the year | No | N/A | Benchmark not notified.
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 90.3 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 82.14 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 83.69 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 72.76 | % of cases resolved within specified time/standard | Yes | No | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | The Commission would notify the target levels for these indices annually based on Licensee info. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available.
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | Voltage Variation (Unbalance) | Maintenance of voltage at supply point within stipulated limits. | Resolution of complaints; Voltage unbalance limit at supply point. | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | 98.22 | % of cases resolved within specified time/standard | Yes | Yes | Different standard metric
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | N/A | N/A | N/A | N/A | N/A | No | N/A | Data is not reported.
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in urban areas. | 95 | % of cases to be resolved within specified time/standard | 96.89 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas [ts.pdf]. | 95 | % of cases to be resolved within specified time/standard | 96.84 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints within 2 working days (no info) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | 87.02 | % of cases resolved within specified time/standard | Yes | No | N/A

## MPEZ,MADHYA PRADESH
Madhya Pradesh Poorv Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply |  | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within 3% for EHT and 8% for HT consumers | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 90.94 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 87.26 | % of cases resolved within specified time/standard | Yes | No | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPCZ, MADHYA PRADESH
Madhya Pradesh Madhya Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 99.2 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 99 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 98.2 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPWZ,MADHYA PRADESH
Madhya Pradesh Paschim Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004 | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) Regulations, 2012 [No. RG-8(II) of 2012] | Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) (Revision-II) (First Amendment) Regulations, 2012 {ARG-8(II )(i) of 2021}.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported in the summary performance table.
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2022-23 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data not reported.
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## CESC, KARNATAKA
Chamundeshwari Electricity Supply Corporation Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95% | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available

## BESCOM, KARNATAKA
Bangalore Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95% | Minimum percentage of cases that must be resolved within the specified 7-day time limit | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | Minimum percentage of failed transformers that must be replaced within the specified time. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available

## HESCOM, KARNATAKA
Hubli Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available

## GESCOM, KARNATAKA
Gulbarga Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available

## MESCOM, KARNATAKA
Mangalore Electricity Supply Company Limited
Karnataka Electricity Regulatory Commission Licensees' Standards of Performance) Regulations - 2004 | Karnataka Electricity Regulatory Commission (Rights of Consumers Relating to Supply of Electricity, Standards of Performance (SoP) and allied matters) Regulations, 2022.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption | Based on info provided by Licensees, the Commission may notify target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Variation limits: LT ±6%; HT +6%/-9%; EHV ±12.5%. Resolution (no network expansion) within 7 days | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Cities and Towns,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 72 hours in Rural areas,. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 hours if no info is required, or 7 days if additional information is needed | 99 | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available

## TANGEDCO, TAMIL NADU
Tamil Nadu Generation and Distribution Corporation Limited
TAMIL NADU ELECTRICITY DISTRIBUTION STANDARDS OF PERFORMANCE REGULATIONS, 2004 (As amended upto 31-03-2024)
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours to 120 days depending on network needs. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Arithmetic errors within the due date; other complaints resolved before the next billing cycle. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours to 120 days depending on network needs. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Arithmetic errors within the due date; other complaints resolved before the next billing cycle. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours to 120 days depending on network needs. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Arithmetic errors within the due date; other complaints resolved before the next billing cycle. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours to 120 days depending on network needs. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Arithmetic errors within the due date; other complaints resolved before the next billing cycle. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Monthly limits of 600 minutes (Urban) or 1200 minutes (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Monthly limits of 15 interruptions (Urban) or 25 interruptions (Rural). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Momentary outages of duration less than five minutes are specifically excluded from reliability index calculations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Variation limits: Single/Three Phase & 11/22kV (+6% to -10%). Rectification within 48 hours to 120 days depending on network needs. | 90 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Distortions in the power supply. | Not specified with a numeric standard in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power supply by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Corporation and Urban areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power supply by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural and Hill areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Arithmetic errors within the due date; other complaints resolved before the next billing cycle. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## NBPDCL, BIHAR
North Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## SBPDCL, BIHAR
South Bihar Power Distribution Company Limited
Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) Regulations, 2006 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2012 | Bihar Electricity Regulatory Commission (Standards of Performance of Distribution Licensee) (First Amendment) Regulations, 2017
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | Target levels determined annually by the Bihar Electricity Regulatory Commission. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution within 10 days (no expansion) or 120 days (up-gradation). | 98 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Licensee must investigate and reduce harmonics on receipt of a complaint from a consumer. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in Cities and Towns. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 72 hours in Rural areas. | 95 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 24 working hours (no info needed) or 7-15 days (if info/inspection needed). | 99 | % of cases to be resolved within specified time/standard | N/A | N/A | No | N/A | Reported data not available

## WBSEDCL, WEST BENGAL
West Bengal State Electricity Distribution Company Limited
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) Regulations, 2010
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) (First Amendment) Regulations, 2013.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available

## DPL, WEST BENGAL
The Durgapur Projects Limited
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) Regulations, 2010
West Bengal Electricity Regulatory Commission (Standards of Performance of Licensees Relating to Consumer Services) (First Amendment) Regulations, 2013.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission shall make reliability calculations and check for compliance with requirements under the Tariff Regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits. | Take corrective measures within 15 days if the problem is local, or within 6 months if system augmentation is required. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Restoration of supply through a transformer within 12 hours in Urban areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Restoration of supply through a transformer within 48 hours in Rural areas. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available

## PVVNL, UP
Paschimanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## MVVNL,UP
Madhyanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## DVVNL,UP
Dakshinanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## PuVVNL,UP
Purvanchal Vidyut Vitran Nigam Limited
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## KESCO,UP
Kanpur Electricity Supply Company
Uttar Pradesh Electricity Regulatory Commission (Standards of Performance) Regulations, 2019
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APSPDCL, AP
Southern Power Distribution Company of Andhra Pradesh Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APEPDCL,AP
Eastern Power Distribution Company of Andhra Pradesh Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%.N/A | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available

## APCPDCL,AP
Andhra Pradesh Central Power Distribution Corporation Limited
Andhra Pradesh Electricity Regulatory Commission (Licensees’ Standards of Performance) Regulation, 2004 | APERC (Licensees' Standards of Performance Second Amendment) Regulation, 2013 | APERC (Licensees' Standards of Performance) Fourth Amendment Regulation, 2023 | Fifth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2024 | Sixth Amendment to Andhra Pradesh Electricity Regulatory Commission (Licensees' Standards of Performance) Regulation, 2025
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2025-26 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 30 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 85 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2025-26 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2025-26 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2024-25 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2024-25 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+) : 3%; Stage-2 (33KV) : 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2024-25 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2023-24 | Reliability of Supply | SAIDI | Average duration of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 20 | Duration of interruption per comsumer per year (hh:mm) | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | SAIFI | Average frequency of sustained interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | 72 | Number of interruptions per consumer per year | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | MAIFI | Average frequency of momentary power interruptions per consumer in a year. | Based on the information provided by the Licensees, the Commission would notify the target levels for these indices annually | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Reliability of Supply | CAIDI | Average duration of interruption for consumers who experienced an interruption. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2023-24 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Within 10 days if no expansion/ enhancement of network involved, Within 120 days if up-gradation of distribution system required | 3 | Maximum allowable voltage unbalance at the point of commencement of supply. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Quality of Supply | Harmonics | Distortions in the power supply. | Stage-1 (132KV+): 3%; Stage-2 (33KV): 8%; Stage-3 (11KV): 8%. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 24 hours in towns and cities. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in rural areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2023-24 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 working hours (no info needed) or 7 working days (if info needed). | 0.1 | Maximum % of faulty bills relative to the total number of bills issued. | N/A | N/A | No | N/A | Reported data not available
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2022-23 | Reliability of Supply | SAIDI | Average total duration of all sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | SAIFI | Average number of sustained power interruptions experienced by a consumer in a month. | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | The Commission will fix target levels for reliability indices annually based on licensee information. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Voltage Variation | Maintenance of voltage at supply point within stipulated limits. | Limits: LT ±6%; HT +6%/-9%; EHV +10%/-12.5%. Resolution: 2 days (local), 10 days (no expansion), 120 days (up-gradation). | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Not specified in the provided regulations. | N/A | N/A | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Urban | Restoration of power by replacing failed transformers in urban areas. | Replacement of failed distribution transformers within 8 hours in Urban Areas (6 hours in Class-I cities). | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Restoration of Supply | Distribution Transformer Failure: Rural | Restoration of power by replacing failed transformers in rural areas. | Replacement of failed distribution transformers within 48 hours in Rural Areas. | 95 | % of cases to be resolved within specified time/standard. | N/A | N/A | No | N/A | Reported data not available
2022-23 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve complaints as per the provisions of section 6.5 of UPERC Electricity Supply Code. | 0.1 | Maximum % of bills requiring modifications following complaints relative to total bills issued. | N/A | N/A | No | N/A | Reported data not available