## MSEDCL,MAHARASHTRA
Maharashtra State Electricity Distribution Company Limited
Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) Regulations, 2021
Maharashtra Electricity Regulatory Commission (Electricity Supply Code and Standards of Performance of Distribution Licensees including Power Quality) (First Amendment) Regulations, 2024.
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark specified for the standard meaning | Reported data | Reported data meaning | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | N/A | N/A | N/A | 887.54 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | N/A | N/A | N/A | 5.6 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Standard for momentary outages was not yet effective for 2021-22 cycle. | N/A | N/A | N/A | Data for momentary interruptions was not reported in this period. | No | N/A | Reporting mandated starting July 2024.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | N/A | N/A | N/A | 624.24 | Average time in minutes taken to restore supply for each interruption event over the year | No | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Maintaining supply voltage at consumer terminals within limits of Un +10% / -15%. | Maintain within limits for 100% of the time. | N/A | 13.6% | % of cases resolved within specified time/standard | No | N/A | Performance data not reported in this specific benchmark format.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A | N/A | N/A | N/A | No | N/A | Performance Data not provided.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Resolve within 24 hrs (receipt) or during subsequent cycle. | 99 | % of cases to be resolved within specified time/standard | 74.55% | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 18 hours in Urban areas. | 90 | % of cases to be resolved within specified time/standard | 18.29% | % of cases resolved within specified time/standard | Yes | No | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply. | Restoration must occur within 48 hours in Rural areas. | 90 | % of cases to be resolved within specified time/standard | 23.16% | % of cases resolved within specified time/standard | Yes | No | N/A

## DGCVL,GUJARAT
Dakshin Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023.
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 6:19 | Total duration (Hr:Min) of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4.61 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 10.13 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions. | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 82.21 | Average restoration time (Minutes) for interrupted consumers over the year | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. Resolve network issues in 60-180 days. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | N/A | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.81 | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 82.15% | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## MGVCL,GUJARAT
Madhya Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023.
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 4:48 | Total duration (Hr:Min) of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 3.79 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 9.82 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 76 | Calculated average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | N/A | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 5.39% | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 50.39% | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## UGVCL,GUJARAT
Uttar Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023.
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 36:33 | Total duration (Hr:Min) of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 30.14 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 64.73 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 72.76 | Calculated average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 97.11% | % of sample tests showing NIL deviation from prescribed standards. | N/A | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 99.93% | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 6.88% | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 29.66% | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.

## PGVCL,GUJARAT
Paschim Gujarat Vij Company Limited
Gujarat Electricity Regulatory Commission (Standards of Performance of Distribution Licensees) Regulations, 2023.
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 209:08 | Total duration (Hr:Min) of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 95.34 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 114.17 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | N/A | N/A | 131.61 | Calculated average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | N/A | N/A | No benchmark defined in regulations.
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3.5% for LT consumers; 3.0% for HT and EHT consumers. | N/A | N/A | 100% | % of sample tests showing NIL deviation from prescribed standards. | NO | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | N/A | N/A | 2.8% | % failure rate of Distribution transformer | NO | N/A | No benchmark defined in regulations.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | N/A | N/A | 41.44% | % of cases resolved within specified time/standard during the year. | NO | N/A | No benchmark defined in regulations.
Year | Indicator Type | Indicator | Standard Specified | Benchmark specified for the standard | Reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | 209:08 | Total duration (Hr:Min) of sustained interruptions for an average consumer over the year. | NO | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | 95.34 | Total number of sustained interruptions for an average consumer over the year. | NO | N/A
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | Targets set by the Commission through separate guidelines/order. | 114.17 | Total number of momentary interruptions for an average consumer over the year. | NO | N/A
2021-22 | Reliability of Supply | CAIDI | Average restoration time for those consumers who experienced sustained interruptions | Targets set by the Commission through separate guidelines/order. | 131.61 | Calculated average restoration time (Minutes) for interrupted consumers over the year. | NO | N/A
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | LV: ± 6%; HV: +6% & -9%; EHV: +10% & -12.5%. | 100% | % of sample tests showing NIL deviation from prescribed standards. | YES | YES
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3.5% for LT consumers; 3.0% for HT and EHT consumers. | 100% | % of sample tests showing NIL deviation from prescribed standards. | YES | YES
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers | Within 6 hours in Urban areas and 24 hours in Rural areas. | 2.8% | % failure rate of Distribution transformer. | NO | YES
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers | Same Day (no info); 10 days (info needed); 15 days (site visit). | 41.44% | % of cases resolved within specified time/standard during the year. | NO

## MPEZ,MADHYA PRADESH
Madhya Pradesh Poorv Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark specified for the standard meaning | Reported data | Reported data meaning | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPWZ,MADHYA PRADESH
Madhya Pradesh Paschim Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark specified for the standard meaning | Reported data | Reported data meaning | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A

## MPCZ, MADHYA PRADESH
Madhya Pradesh Madhya Kshetra Vidyut Vitaran Company Limited
Madhya Pradesh Electricity Regulatory Commission (Distribution Performance Standards) Regulations, 2004
Year | Indicator Type | Indicator | Indicator meaning | Standard Specified | Benchmark specified for the standard | Benchmark specified for the standard meaning | Reported data | Reported data meaning | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a month | To be laid down by the Commission after analysis of data furnished by Licensee | Not specified | Not specified | N/A | N/A | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | VOLTAGE VARIATION | Maintenance of voltage at the point of supply within stipulated limits | Licensees must resolve variation complaints within 10 days (no network expansion) or 180 days (up-gradation required) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Quality of Supply | HARMONICS | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within limits (3% for EHT and 8% for HT consumers) | Not specified | Not specified | N/A | N/A | No | N/A | Performance data for this index was not included in the 2021-22 performance report.
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Urban | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 5 days (if info is needed) | 99 | % of cases to be resolved within specified time/standard | 99.2 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution : Rural | Resolution of billing problems reported by consumers. | Resolve billing complaints on the same day (no info required) or within 10 days (if info is needed | 99 | % of cases to be resolved within specified time/standard | 99 | % of cases resolved within specified time/standard | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Urban | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Replacement or restoration must occur within 24 hours (or 12 hours in HQ) of the failure | 90 | % of cases to be resolved within specified time/standard | 100 | % of cases resolved against the benchmark | Yes | Yes | N/A
2021-22 | Restoration of Supply | Distribution Transformer Failure : Rural | Restoration of power by replacing failed transformers or providing alternate supply arrangements | Restoration within 48 hours; replacement within 72 hours (dry weather) or 7 days (monsoon) | 90 | % of cases to be resolved within specified time/standard | 98.2 | % of cases resolved against the benchmark | Yes | Yes | N/A

## AVVNL,RAJASTHAN
Ajmer Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 36.8 | Total hours of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 31.07 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 98.98% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A |  | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Data not provided in quarterly performance returns
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 99.11% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.12% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JVVNL,RAJASTHAN
Jaipur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A |  | Total hours of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A |  | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A |  | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A |  | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. |  | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A |  |  | Data for harmonic levels was not reported in this period. | No | N/A | Data not provided in quarterly performance returns
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. |  | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. |  | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## JVVNL,RAJ
Jodhpur Vidyut Vitran Nigam Limited
RERC ( Standards of Performance for Distribution Licensees) Regulations, 2021
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard |  | Reported data |  | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Thirty hours per consumers per six months or fifteen hours per consumer per quarter . | N/A | N/A | 21.79 | Total hours of supply interruption for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Twenty interruptions per consumer per six months or ten interruptions per consumer per quarter . | N/A | N/A | 12.15 | Total number of sustained interruptions for an average consumer over the year. | Yes | Yes | N/A
2021-22 | Reliability of Supply | MAIFI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | No | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits (+6% to -9% (LT/HT). | Resolve within 2 to 120 days depending on required work. | 90 | % of cases to be resolved within specified time/standard. | 97.43% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | Maintenance of Total Harmonic Distortion in Voltage (THDV) within3% for EHT; 8% for HT | N/A |  | N/A | Data for harmonic levels was not reported in this period. | No | N/A | Data not provided in quarterly performance returns
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power by replacing failed distribution transformers. | Within 8 hrs (Class-1/Urban), 24 hrs (Rural). | 90 | % of cases to be resolved within specified time/standard. | 96.78% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | Within 3 working days (no info needed) or 7 working days (if info needed). | 90 | % of cases to be resolved within specified time/standard. | 98.36% | % of cases resolved within specified time/standard during the year. | Yes | Yes | N/A

## TPCODL,ODISHA
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard | Meaning of the Benchmark specified | Reported data | Meaning of the reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 9304 | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 378 | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A | 85 | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A (Individual complaint-based indicator) | 0 | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
| Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A | N/A | N/A | N/A | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas and 48 hours in Rural areas. | 95% | Minimum percentage of failed transformers that must be replaced within the specified time. | 95.98% | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | Not more than 0.1% | Maximum allowable percentage of faulty bills relative to the total number of bills issued. | 0.46% | Out of all bills issued, 0.46% were faulty or required active rectification. | Yes | No | N/A

## TPNODL,ODISHA
Tata Power North Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard | Meaning of the Benchmark specified | Reported data | Meaning of the reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A |  | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A (Individual complaint-based indicator) |  | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
| Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A |  | N/A | N/A | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas and 48 hours in Rural areas. | 95% | Minimum percentage of failed transformers that must be replaced within the specified time. |  | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | Not more than 0.1% | Maximum allowable percentage of faulty bills relative to the total number of bills issued. |  | Out of all bills issued, 0.46% were faulty or required active rectification. | Yes | No | N/A

## Sheet13
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard | Meaning of the Benchmark specified | Reported data | Meaning of the reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A |  | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A (Individual complaint-based indicator) |  | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
| Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A |  | N/A | N/A | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas and 48 hours in Rural areas. | 95% | Minimum percentage of failed transformers that must be replaced within the specified time. |  | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | Not more than 0.1% | Maximum allowable percentage of faulty bills relative to the total number of bills issued. |  | Out of all bills issued, 0.46% were faulty or required active rectification. | Yes | No | N/A

## Sheet14
Tata Power Central Odisha Distribution Limited
ORISSA ELECTRICITY REGULATORY COMMISSION (LICENSEES' STANDARDS OF PERFORMANCE) REGULATIONS, 2004
Year | Indicator Type | Indicator |  | Standard Specified | Benchmark specified for the standard | Meaning of the Benchmark specified | Reported data | Meaning of the reported data | Comparison Possible? | Standard met? | If comparison not possible, why?
2021-22 | Reliability of Supply | SAIDI | The average total duration of all sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total minutes of supply interruption for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | SAIFI | The average number of sustained power interruptions experienced by a consumer in a month | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of sustained interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | MAIFI | The average number of momentary interruptions experienced by a consumer in a mont | Based on the information provided by the Licensees, the Commission may notify the target levels for these indices annually | N/A | N/A |  | Total number of average interruptions for an average consumer over the year. | No | N/A | No benchmark defined in regulations.
2021-22 | Reliability of Supply | CAIDI | Not listed for overall standard reporting in the regulation. | N/A | N/A | N/A |  | N/A | N/A | N/A | Not listed for overall standard reporting in the regulation.
2021-22 | Quality of Supply | Voltage Variation | Maintenance of voltage at the point of supply within stipulated limits | Low/Medium Voltage: ±6%<br>High Voltage: +6% to -9%<br>Extra High Voltage: +10% to -12.5%. | N/A | N/A (Individual complaint-based indicator) |  | zero formal consumer complaints recieved | No | N/A | No complaints were received or registered during the year.
| Quality of Supply | Harmonics | Unwanted electrical vibrations that distort the power supply | 3% - 132KV, 8% -11KV/ 33KV | N/A | N/A |  | N/A | N/A | N/A | No benchmark defined in regulations.
2021-22 | Restoration of Supply | Transformer Failure | Restoration of power supply by replacing failed distribution transformers within time limits. | Replacement of failed distribution transformers within 24 hours in Urban areas and 48 hours in Rural areas. | 95% | Minimum percentage of failed transformers that must be replaced within the specified time. |  | % of cases resolved within specified time/standard during the year. | Yes | No | N/A
2021-22 | Consumer Bill Complaint | Billing Complaint Resolution | Resolution of billing problems reported by consumers. | The licensee shall resolve the complaint regarding electricity bills within 30 days of its receipt. | Not more than 0.1% | Maximum allowable percentage of faulty bills relative to the total number of bills issued. |  | Out of all bills issued, 0.46% were faulty or required active rectification. | Yes | No | N/A